LPG Facilities Audit Checklist

The audit intent is to inspect and review design and placement of facility spacing and drainage, fire protection, equipment installation and construction design, conducted in accordance with appropriate regulations and standards applicable to customers country.

The items of the form will vary depending on the home country of the customer and in some cases it is necessary to determine whether the structure, equipment or working practice is suitable for use to provide a safe working environment.

Conditions, monitored discrepancies and problems must be noted in the ''Comments'' column. Facility representative should be present during the survey.

Facility location, address     ________________________________________________

Name of a facility ________________________________________________

Facility representative _____________________________________________

Facility representative _____________________________________________

Date of an audit _____________

| # | Items |  |  |  | Comments |
| --- | --- | --- | --- | --- | --- |
| # Tank storage |  |  |  |  |  |
|  | Number and capacity of tanks for storing propane and butane? |  |  |  |  |
|  | Tanks certification period. - Next test |  |  |  |  |
|  | Is there a system preventing tank overflow in the facility |  |  |  |  |
|  | Is there impound in the tanks for storing hydrocarbons? |  |  |  |  |
|  | Is the area inside the tank impound free of weeds, combustible materials and debris? |  |  |  |  |
|  | Are the drainage paths from the tanks sloped at minimum 1% grade away from personnel traffic areas, tanks and piping? |  |  |  |  |
|  | Is there a procedure for annual test and service of pressure safety valves? When were these PSVs last audited? |  |  |  |  |
|  | Is there a procedure for annual maintenance of ring spray and fire fighting foam systems? When was this procedure last audited? |  |  |  |  |
|  | Which means of communication are used? |  |  |  |  |
| # Fire protection |  |  |  |  |  |
|  | Lightning arrester |  |  |  |  |
|  | Fire alarm unit, warning system |  |  |  |  |
|  | Fire extinguishers inspection schedule |  |  |  |  |
|  | Is there emergency response plan? Are they updated? Do scenarios correspond to facilities? |  |  |  |  |
|  | Are there drills conducted for emergency response? When was the last drill? |  |  |  |  |
|  | Training workers within the emergency response plan |  |  |  |  |
|  | Does the facility have an adequate primary supply of firewater? Guidelines are: · 6 hr. supply at 379 - 505 l/s for LPG storage & loading facilities (Liquefied petroleum gas) |  |  |  |  |
|  | Does the facility have an adequate alternative source of firewater? If so, are reservoirs kept full? Capacity and number of reservoirs with water? |  |  |  |  |
|  | Complete set of fire fighting board |  |  |  |  |
|  | Are there pumps for firefighting in the facility? Number Capacity |  |  |  |  |
|  | Are firefighting pumps tested annually? |  |  |  |  |
|  | Do fire hydrants have leaks? |  |  |  |  |
|  | Do fire hydrant block valve pits fill up with water? Does the facility have a procedure to keep them pumped out? |  |  |  |  |
|  | Does the facility have a procedure to keep hydrants from freezing in the winter? |  |  |  |  |
|  | Are fire hydrants labeled? |  |  |  |  |
|  | Are fire water system flow rates and pressures adequate? Pressure should be maintained continuously at 4-7 ATM. |  |  |  |  |
|  | Do firewater pumps have an uninterruptable power supply (e.g., a back-up generator), or diesel engine drivers? |  |  |  |  |
|  | Instructions for conducting hot works |  |  |  |  |
|  | Does the facility have a procedure to inform the fire department when the fire water system is out of service or impaired? |  |  |  |  |
|  | Is each valve cycled at least once a year? |  |  |  |  |
| First aid fire hose |  |  |  |  |  |
|  | Are first aid fire hoses installed in appropriate locations? · Within 6 m and 15 m of the hazard. · Recommended for installation in process units, near pumps, manifold, other critical equipment; loading racks, and process buildings. |  |  |  |  |
|  | Are first aid fire hoses maintained properly? · All parts are present & not corroded · No hose leaks or rot · Proper size hose connectors · Block valve operable · Hose reel drum rotates · No freeze damage |  |  |  |  |
|  | Are fire hose locations well marked? |  |  |  |  |
|  | Is there unobstructed access to first aid fire hoses? |  |  |  |  |
|  | Does the facility have a procedure to test fire hoses annually? Are inspection records available? |  |  |  |  |
| Fixed spray system |  |  |  |  |  |
|  | Are fixed spray systems necessary? |  |  |  |  |
|  | Are there records on testing spray systems? |  |  |  |  |
|  | Type of gas detector, operational suitability |  |  |  |  |
|  | Do detectors have reserve power supply? |  |  |  |  |
|  | Inspection and technical maintenance of the detector |  |  |  |  |
|  | Are ventilation systems inside process buildings with fixed fire suppression systems (foam or water sprays) interlocked with fire alarm system so that ventilation systems will shut down when alarms are activated? |  |  |  |  |
| Emergency Vehicle Access |  |  |  |  |  |
|  | Location of the nearest fire station, km |  |  |  |  |
|  | Is there sufficient access for emergency vehicles? · Road width adequate · Turn radius adequate · Multiple approach paths |  |  |  |  |
|  | Is vertical clearance adequate? |  |  |  |  |
|  | Is breathing air equipment well maintained? Are maintenance records available? |  |  |  |  |
|  | Are personnel trained in the safe operation and limitations of breathing air equipment? |  |  |  |  |
|  | Are emergency alarms hard-wired to the fire station? If so, are they tested periodically? Are inspection records available? |  |  |  |  |
|  | Are environmentally sensitive liquid waste streams segregated from storm sewer drainage systems? |  |  |  |  |
|  | Are there appropriate protection devices, personal protection equipment and procedures for treating hazardous materials at the facility? |  |  |  |  |
| Loading \ Unloading rack |  |  |  |  |  |
| 49 |  | Nearest railway station, km |  |  |  |
| 50 |  | How storage tanks and reservoirs are controlled for - Arrival - Departure - Drainage to storage reservoirs - residual pressure - reservoir load-line |  |  |  |
| 51 |  | Availability of parking place for RTCs, number or railcars for single parking at the terminal |  |  |  |
| 52 |  | RTC unloading rate - per hour - per day |  |  |  |
| 53 |  | Is there LPG unloading procedure, if yes, then, present the document. |  |  |  |
| 54 |  | Is there in the rack - rope cutters - shoes - grounding (acts) |  |  |  |
| 55 |  | How many points for unloading |  |  |  |
| 56 |  | How LPG volume is checked unloaded from RTCs? |  |  |  |
| 57 |  | Railway weigh station, certification period - next test |  |  |  |
| 58 |  | What else products are unloaded at the discharge rack |  |  |  |
| 59 |  | Hoses are manufactured of rubber-fabric material. When were they last checked? |  |  |  |
| 60 |  | Gauges for measuring pressure |  |  |  |
| # Fire proofing |  |  |  |  |  |
| 61 |  | Are critical pipe supports fire proofed on plot? Does fire proofing extend 20 ft. (6 m) above grade? |  |  |  |
| Equipment and Piping |  |  |  |  |  |
| 62 |  | Pumps - Number - type - operating pressure - output, m3/h |  |  |  |
| 63 |  | Compressors - Number - type - operating pressure - output, m3/h |  |  |  |
| 64 |  | LPG loading rate to the vessel in metric tons - per hour - per day |  |  |  |
| 65 |  | Pipeline from berth to terminal - diameter, - length, - pipeline material |  |  |  |
| 66 |  | Product volume necessary for filling the pipeline in metric tons |  |  |  |
| 67 |  | Product metering station, certification period - Next testing |  |  |  |
| 68 |  | Does the equipment have appropriate labeling? |  |  |  |
| 69 |  | Do LPG samplers have double valves? |  |  |  |
| 70 |  | Do pipings have appropriate labeling or color code? Is flow direction marked clearly? |  |  |  |
| 71 |  | Is there any signs of piping leakage? |  |  |  |
| 72 |  | Do distributors seals leak? Is there any excessive leak from pump sealing? |  |  |  |
| Berth |  |  |  |  |  |
| 73 |  |  | - Dimensions in meters - Location and number of berths - Depth in metric tons - Open, separately located berth - Protected (from wind), located adjacent to another (which) berth |  |  |
| 74 |  |  | Vessel type - Max dimensions - Min dimensions - Refrigerator/semi-refrigerator - pressurized |  |  |
| 75 |  |  | Loading arm - number - diamter - throughput |  |  |
| 76 |  |  | Ability of simultaneous loading - Of two vessels from two different berths - Different products (propane\butane) |  |  |
| 77 |  |  | Control of vessels approaching |  |  |
| 78 |  |  | Communication - Berth-vessel - Berth-control room (terminal dispatcher’s room), pump house - Is there vessels loading register kept by the dispatcher’s |  |  |
| Lighting |  |  |  |  |  |
| 79 |  |  |  | Are light levels adequate? · in process buildings, at loading racks, in hallways, stairwells, and lobbies · in exterior plant & off-plot process areas |  |
| 80 |  |  |  | lightning of the rack explosion-proof, allows to ensure unloading\loading operations at day and night |  |
| 81 |  |  |  | Do night operators have intrinsically safe flashlights available? Are lights inside electrically classified areas equipped with vapor covers? |  |
| 82 |  |  |  | Does the facility have an emergency shutdown system? If not, is there a manual shutdown procedure? When was this procedure last audited? |  |
| 83 |  |  |  | Is there a procedure to test the emergency shutdown system & alarm system periodically? Are operators trained in the testing procedures? |  |
| 84 |  |  |  | Is there a procedure to test process alarms monthly? When was this procedure last audited? |  |
| # General requirements |  |  |  |  |  |
| 85 |  |  |  | Safety specialist in the staff list |  |
| 86 |  |  |  | Investigation of incidents |  |
| 87 |  |  |  | Personal protection equipment - breathing apparatus - coveralls - glasses, masks - shoes - earplugs - gloves - hardhat |  |
| 88 |  |  |  | Are there any procedure of personnel admittance to a LPG facility |  |
|  |  |  |  | Is there procedure of an usage of portable electronic devises - Cell phone - Cameras - Flashlights - Pagers |  |
| 90 |  |  |  | Are there warming signs : '' No smoking'', ''Stop'' |  |